## Design Basis
SWS — 40 ft High-Cube E-House · SCADA Room — HVAC Design Basis
Legend: blue = input you may change · yellow fill = key assumption to confirm · black = formula · green = link from another sheet
Status: FOR REVIEW — design basis assumptions must be confirmed by SWS Engineering before procurement.
Ref | Parameter | Value | Unit | Source / note
CLIMATE
DB-01 | Outdoor design dry bulb | 50 | °C | Conservative Eastern Province shelter design ambient (ASHRAE 0.4% for Dammam is ≈46 °C). Confirm against project HVAC spec.
DB-02 | Outdoor design humidity ratio | 22 | g/kg | Coastal humid design condition, Dammam (assumed).
DB-03 | Indoor design dry bulb | 24 | °C | Typical for SCADA / control equipment rooms (24 ± 2 °C).
DB-04 | Indoor humidity ratio (≈50 % RH @ 24 °C) | 9.3 | g/kg | Psychrometric value at 24 °C / 50 % RH.
GEOMETRY (from GA drawing SWS-2286 Rev 0)
DB-05 | External length | 12.192 | m | GA sheet 1: 12,192 mm.
DB-06 | External width | 2.438 | m | 40 ft HC container standard width.
DB-07 | External height | 2.894 | m | GA sheet 1: 2,894 mm.
DB-08 | Sandwich panel thickness | 0.05 | m | Insulated wall/roof panel (assumed 50 mm PU).
DB-09 | Internal clear height | 2.55 | m | Assumed after floor build-up and ceiling panel.
ENVELOPE
DB-10 | U-value walls & roof | 0.45 | W/m²K | 50 mm PU sandwich panel incl. surface films (assumed).
DB-11 | U-value floor | 0.6 | W/m²K | Checker plate on insulated floor, shaded by skid (assumed).
DB-12 | Solar allowance — roof | 20 | K | Added to ΔT; light-coloured roof (CLTD-simplified).
DB-13 | Solar allowance — walls | 10 | K | Added to ΔT; light-coloured walls (CLTD-simplified).
DB-14 | Thermal bridging / door allowance | 10% | — | Fraction added to envelope gain.
INTERNAL GAINS
DB-15 | Equipment heat dissipation (SCADA panels, UPS, DBs) | 6 | kW | PLACEHOLDER — replace with electrical heat-dissipation list. Dominant load.
DB-16 | Lighting power density | 10 | W/m² | LED lighting.
DB-17 | Occupants (maintenance) | 2 | persons | Intermittent occupancy.
DB-18 | Sensible heat per person | 75 | W | ASHRAE, seated/light work.
DB-19 | Latent heat per person | 55 | W | ASHRAE, seated/light work.
AIR
DB-20 | Fresh air per person | 10 | L/s | Minimum outdoor air for occupants (assumed).
DB-21 | Infiltration | 0.3 | ACH | Tight shelter, positive pressure (assumed).
SELECTION
DB-22 | Safety factor on design load | 10% | — | Design margin.
DB-23 | Number of A/C units installed | 3 | units | As built: 3 split A/C units (project scope).
DB-24 | Standby units (redundancy) | 1 | units | N+1: one unit on standby / duty rotation.
DB-25 | Capacity derating at design ambient | 80% | — | Fraction of nominal (T1) capacity available at design ambient; use T3 (tropical) rated units. Confirm with manufacturer data.

## Heat Load
Cooling load calculation — SCADA Room (steady-state, design day)
All values in W unless stated. Inputs are linked from the Design Basis sheet (green).
Item | Basis | Quantity | Unit | Sensible (W) | Latent (W)
Design ΔT (outdoor − indoor) | DB-01 − DB-03 | 26 | K
Roof area | L × W | 29.7241 | m²
Wall area (long + end walls) | 2(L+W) × H | 84.6784 | m²
Floor area (external) | L × W | 29.7241 | m²
Internal floor area | (L−2t)(W−2t) | 28.2711 | m²
Internal volume | internal area × clear height | 72.0913 | m³
Roof conduction + solar | U × A × (ΔT + solar roof) |  |  | 615.2888 | 0
Wall conduction + solar | U × A × (ΔT + solar walls) |  |  | 1371.7907 | 0
Floor conduction (shaded) | U floor × A × ΔT |  |  | 463.6959 | 0
Thermal bridging / doors | allowance × envelope |  |  | 245.0775 | 0
Equipment heat dissipation | DB-15 × 1000 |  |  | 6000 | 0
Lighting | LPD × internal area |  |  | 282.711 | 0
Occupants | n × sensible / latent |  |  | 150 | 110
Fresh air | Q = n × L/s; 1.207·Q·ΔT ; 3.0·Q·Δw | 20 | L/s | 627.64 | 762
Infiltration | Q = ACH × V / 3.6 | 6.0076 | L/s | 188.5308 | 228.8899
Subtotal |  |  |  | 9944.7347 | 1100.8899
Safety factor | DB-22 |  |  | 994.4735 | 110.089
DESIGN COOLING LOAD |  |  |  | 10939.2081 | 1210.9788
Total design load |  | 12.1502 | kW
Total design load |  | 3.4547 | TR
Sensible heat ratio |  | 0.90033
Equipment share of load |  | 54.32%
Method: simplified steady-state CLTD approach (ASHRAE Fundamentals). Air constants: sensible 1.207 W/(L/s·K), latent 3.0 W/(L/s·g/kg).

## Unit Selection
A/C unit selection — N+1 redundancy check
Design load to cover |  | 12.1502 | kW
Units installed |  | 3
Units running (N = installed − standby) |  | 2
Derating at design ambient |  | 80%
Nominal size (TR) | Nominal capacity (kW) | Capacity at design ambient (kW) | Running units total (kW) | Covers load with 1 standby? | Capacity margin
1.5 | 5.2755 | 4.2204 | 8.4408 | NO | -30.53%
2 | 7.034 | 5.6272 | 11.2544 | NO | -7.373%
2.5 | 8.7925 | 7.034 | 14.068 | YES | 15.78%
3 | 10.551 | 8.4408 | 16.8816 | YES | 38.94%
4 | 14.068 | 11.2544 | 22.5088 | YES | 85.25%
Selected nominal size per unit |  | 2.5
Selected nominal capacity per unit |  | 8.7925 | kW
Installed capacity, all units running (at design ambient) |  | 21.102 | kW
Capacity with one unit on standby (at design ambient) |  | 14.068 | kW
Rule: smallest nominal size whose running units (N) cover the design load at design ambient. Use T3 (tropical) rated, R410A/R32 split units with low-ambient and high-ambient protection.

## Equipment Schedule
HVAC equipment schedule — SCADA Room
Tag | Type | Location (from left end, m) | Nominal size (TR) | Nominal capacity (kW) | Mounting | Notes
AC-01-IDU | Split A/C — indoor unit | 2.83 | 2.5 | 8.7925 | Wall-mounted split indoor unit, high level (≈2.2 m) | Lead/lag rotation; F&G trip on fire alarm
AC-01-ODU | Split A/C — outdoor condensing unit | 2.83 | 2.5 | 8.7925 | External wall bracket, galvanised mesh guard (per GA) | T3 rated; condensate & refrigerant via sealed wall sleeve
AC-02-IDU | Split A/C — indoor unit | 6.21 | 2.5 | 8.7925 | Wall-mounted split indoor unit, high level (≈2.2 m) | Lead/lag rotation; F&G trip on fire alarm
AC-02-ODU | Split A/C — outdoor condensing unit | 6.21 | 2.5 | 8.7925 | External wall bracket, galvanised mesh guard (per GA) | T3 rated; condensate & refrigerant via sealed wall sleeve
AC-03-IDU | Split A/C — indoor unit | 9.43 | 2.5 | 8.7925 | Wall-mounted split indoor unit, high level (≈2.2 m) | Lead/lag rotation; F&G trip on fire alarm
AC-03-ODU | Split A/C — outdoor condensing unit | 9.43 | 2.5 | 8.7925 | External wall bracket, galvanised mesh guard (per GA) | T3 rated; condensate & refrigerant via sealed wall sleeve
CTRL-01 | Lead/lag (duty-standby) controller with room thermostat |  |  |  | Inside, next to entrance door, 1.5 m AFL | Rotates duty unit every 24 h; starts standby on high temperature (28 °C) or unit fault; alarm to SCADA
Unit positions measured from the A/C outdoor openings on GA sheet 1 elevation (SWS-2286 Rev 0); confirm on site.

## Notes & Assumptions
Notes & assumptions
1. SCOPE: Cooling load and A/C sizing for the 40 ft high-cube SCADA Room E-House (one of three E-Houses in the package).
2. GEOMETRY from GA drawing SWS-2286 Rev 0 (sheets 1–2), issued 22 Sep 2026.
3. KEY ASSUMPTIONS (yellow on Design Basis) must be confirmed: outdoor design condition, panel U-values, equipment heat dissipation and unit derating.
4. EQUIPMENT HEAT DISSIPATION is a placeholder (6.0 kW). It is the dominant load (see Heat Load!C27). Replace with the panel vendor heat-dissipation list.
5. REDUNDANCY: N+1 — any two units must hold the room at 24 °C at design ambient with one unit failed or on standby.
6. UNITS: T3 (tropical) rated split units, R410A or R32, epoxy/Blue-fin coated condenser coils for coastal environment, low-ambient kit, auto-restart after power loss.
7. CONTROLS: lead/lag controller; F&G system trips all A/C units on confirmed fire (per project F&G philosophy); common alarm to SCADA.
8. CONDENSATE: each IDU drained by gravity (min 1:100 fall) to outside through sealed sleeve, discharged clear of the skid and cable trays.
9. This workbook is a design-check tool, not a stamped engineering calculation. Status: FOR REVIEW.